TECHNICAL DATASHEET

2-Pole

7.5kVA – 17.5kVA Range

PERFORMANCE CHARACTERISTICS

| 400/420 V - 50Hz - 3000RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | THREE-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 7.5 | 6 | 7.5 | 25 | 90.2 | 91.5 | 91.3 | 1.5 | 8.5 | 22.32 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 12.5 | 10 | 14 | 46.5 | 92.7 | 93.7 | 93.5 | 1.5 | 15.5 | 33.78 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 17.5 | 14 | 19 | 60 | 95.5 | 94.3 | 95.2 | 1.5 | 20 | 46.59 | 0.0/6.0 | <0.01 |

| 400/420 V - 60Hz - 3600RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | THREE-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 9 | 7.2 | 9 | 25 | 90.2 | 91.5 | 91.3 | 1.5 | 10.2 | 26.78 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 15 | 12 | 16.8 | 46.5 | 92.7 | 93.7 | 93.5 | 1.5 | 18.6 | 40.54 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 20.2 | 16.8 | 22.8 | 60 | 95.5 | 94.3 | 95.2 | 1.5 | 24 | 55.91 | 0.0/6.0 | <0.01 |

| 230/250 V - 50Hz - 3000RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | SINGLE-PHASE DELTA | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 3.1 | 2.5 | 6 | 25 | 77.2 | 82.4 | 84.6 | 1.8 | 8.7 | 7.26 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 6.2 | 5.2 | 12 | 46.5 | 90.4 | 91.8 | 91.5 | 1.6 | 21.6 | 17.86 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 10 | 8 | 18 | 60 | 91.1 | 92.2 | 91.9 | 1.6 | 34.5 | 27.36 | 0.0/6.0 | <0.01 |

| 230/250 V - 60Hz - 3600RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | SINGLE-PHASE DELTA | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 4.8 | 3.8 | 7.2 | 25 | 86.6 | 88.9 | 87.3 | 1.8 | 10.44 | 11.64 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 7.4 | 5.9 | 14.4 | 46.5 | 84.6 | 87.6 | 88.0 | 1.6 | 25.9 | 21.43 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 12 | 9.6 | 21.6 | 60 | 85.7 | 88.2 | 88.5 | 1.6 | 41.4 | 32.82 | 0.0/6.0 | <0.01 |

| CE CERT | FRAME | ENGINE HOUSING | SHAFT COUPLING | INSULATION CLASS | IP RATING |
| --- | --- | --- | --- | --- | --- |
| Yes | 132 |  | V-TAPER 2¼ inch per foot | H | IP23 |

PERFORMANCE DATA – TWO PHASE WINDING

In a RFL Alternator with Two-Phases, the voltages are a 90° out of phase. The peak current and voltages on each phase occurs when the other phase is at its neutral point. The voltages and voltage regulation are independent of each other. A heavy load (motor start) on one phase will have minimal effect on the voltage of the other phase. This is an optional winding configuration designed to utilize maximum power in single phase and is set at the manufacturing stage.

| 230/250 V - 50Hz - 3000RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | TWO-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 7.5 | 6 | 5 | 37.5 | 88.9 | 91.0 | 91.0 | 1.8 | 12.5 | 22.33 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 12.5 | 10 | 9 | 60 | 92.7 | 93.8 | 93.5 | 1.8 | 20 | 33.78 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 17.5 | 14 | 12 | 90 | 93.3 | 94.1 | 93.8 | 1.8 | 30 | 45.23 | 0.0/6.0 | <0.01 |

| 230/250 V - 60Hz - 3600RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | Full (100% Load) | Voltage Transient | Transient Response Time |
|  | TWO-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | A | N.m | +%, -% | ms |
| RF2-7.5 | 9 | 7.2 | 7 | 37.5 | 88.9 | 91.0 | 91.0 | 1.8 | 15 | 26.8 | 0.0/6.0 | <0.01 |
| RF2-12.5 | 15 | 12 | 11 | 60 | 92.7 | 93.8 | 93.5 | 1.8 | 24 | 40.54 | 0.0/6.0 | <0.01 |
| RF2-17.5 | 20.2 | 16.8 | 15 | 90 | 93.3 | 94.1 | 93.8 | 1.8 | 36 | 54.28 | 0.0/6.0 | <0.01 |

TYPICAL ELECTRICAL DATA

|  |  | RF2-7.5 | RF2-12.5 | RF2-17.5 |
| --- | --- | --- | --- | --- |
| Kcc | Short-circuit ratio | 2.95 | 2.95 | 2.95 |
| Xd | Direct-axis synchronous reactance unsaturated | - | - | - |
| Xq | Quadrature-axis synchronous reactance unsaturated | - | - | - |
| T'd | Short-circuit transient time constant | <0.01 | <0.01 | <0.01 |
| T'do | No-load transient time constant | <0.01 | <0.01 | <0.01 |
| Ω | Stator winding resistance |  |  |  |

DIMENSIONS

Model a b Weight mm mm kg RF2-3.75 160 96 19 RF2-7.5 192 128 28 RF2-12.5 237 169 40 RF2-17.5 286 219 51

# Text boxes

15 Waltham Street

Artarmon NSW 2064 AUSTRALIA

SALES@RFLATERNATORS.COM

Tel: +61 02 9584 9970   |   WWW.RFLALTERNATORS.COM

RFL ALTERNATORS

RF2 - SERIES

15 Waltham Street

Artarmon NSW 2064 AUSTRALIA

SALES@RFLATERNATORS.COM

Tel: +61 02 9584 9970   |   WWW.RFLALTERNATORS.COM

RF2 - SERIES

PERMANENT MAGNET ALTERNATOR - BRUSHLESS AND AVR-LESS

RF2 - SERIES

PERMANENT MAGNET ALTERNATOR - BRUSHLESS AND AVR-LESS