TECHNICAL DATASHEET

4-Pole

10kVA – 40kVA Range

Tested to specifications: 	EN 60034-1:2010

EN 60204-1/A1:2009

PERFORMANCE CHARACTERISTICS

| 380/400 V - 50Hz - 1500RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | TEMP: 27°C (Stand By) (ΔT = 60°C) | Full (100%) Load | Voltage Transient | Transient Response Time |
|  | THREE-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | THREE-PHASE | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | kVA | kW | A | N.m | +%, -% | ms |
| RF4-10 | 10 | 8 | 15 | 52 | 91.6 | 92.5 | 90.7 | 2.1 | 11 | 8.8 | 12.9 | 56.1 | 0.0/6.0 | <0.01 |
| RF4-20 | 20 | 16 | 30 | 120 | 92.9 | 93.9 | 93.8 | 2.0 | 22 | 17.6 | 24.9 | 108.6 | 0.0/6.0 | <0.01 |
| RF4-30 | 30 | 24 | 60 | 246 | 93.4 | 94.1 | 94.6 | 2.2 | 33 | 26.4 | 38.0 | 161.3 | 0.0/6.0 | <0.01 |
| RF4-40 | 40 | 32 | 90 | 373 | 93.7 | 94.7 | 94.5 | 2.7 | 44 | 35.2 | 49.3 | 215.3 | 0.0/6.0 | <0.01 |

| 380/400 V - 60Hz - 1800RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | TEMP: 27°C (Stand By) (ΔT = 60°C) | Full (100%) Load | Voltage Transient | Transient Response Time |
|  | THREE-PHASE | MOTOR START | SHORT CIR. | EFFICIENCY | THD | THREE-PHASE | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | kVA | kW | A | N.m | +%, -% | ms |
| RF4-10 | 12 | 9.6 | 18 | 52 | 91.6 | 92.5 | 90.7 | 2.1 | 13.2 | 10.6 | 15.5 | 67.3 | 0.0/6.0 | <0.01 |
| RF4-20 | 24 | 19.2 | 36 | 120 | 92.9 | 93.9 | 93.8 | 2.0 | 26.4 | 21.1 | 30.0 | 130.3 | 0.0/6.0 | <0.01 |
| RF4-30 | 35.5 | 28.4 | 72 | 246 | 93.4 | 94.1 | 94.6 | 2.2 | 39.6 | 31.7 | 45.6 | 193.6 | 0.0/6.0 | <0.01 |
| RF4-40 | 48 | 38.4 | 108 | 373 | 93.7 | 94.7 | 94.5 | 2.7 | 52.8 | 42.2 | 59.2 | 258.4 | 0.0/6.0 | <0.01 |

| 220/240 V - 50Hz - 1500RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | TEMP: 27°C (Stand By) (ΔT = 60°C) | Full (100%) Load | Voltage Transient | Transient Response Time |
|  | SINGLE-PHASE DELTA | MOTOR START | SHORT CIR. | EFFICIENCY | THD | SINGLE-PHASE DELTA | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | kVA | kW | A | N.m | +%, -% | ms |
| RF4-10 | 5 | 4 | 9 | 52 | 85.7 | 86.6 | 85.0 | 5.3 | 6.3 | 5 | 27.3 | 38.7 | 0.0/6.0 | <0.01 |
| RF4-20 | 12.5 | 10 | 20 | 120 | 91.2 | 91.2 | 89.5 | 5.9 | 13.8 | 11 | 49.8 | 71.2 | 0.0/6.0 | <0.01 |
| RF4-30 | 18.8 | 15 | 40 | 246 | 88.6 | 89.7 | 89.4 | 6.4 | 20 | 16 | 74.4 | 107.1 | 0.0/6.0 | <0.01 |
| RF4-40 | 25 | 20 | 60 | 373 | 91.0 | 91.8 | 91.0 | 6.6 | 26.3 | 21 | 98.9 | 139.9 | 0.0/6.0 | <0.01 |

| 220/240 V - 60Hz - 1800RPM |
| --- |
| MODEL | OPERATING TEMP: 40°C (Cont.) (ΔT = 40°C) | TEMP: 27°C (Stand By) (ΔT = 60°C) | Full (100%) Load | Voltage Transient | Transient Response Time |
|  | SINGLE-PHASE DELTA | MOTOR START | SHORT CIR. | EFFICIENCY | THD | SINGLE-PHASE DELTA | Current | Torque |  |  |
|  | kVA | kW | kVA | A | 1/2 | 3/4 | Full | % | kVA | kW | A | N.m | +%, -% | ms |
| RF4-10 | 6 | 4.8 | 10.8 | 52 | 85.7 | 86.6 | 85.0 | 5.3 | 7.5 | 6.0 | 32.8 | 46.4 | 0.0/6.0 | <0.01 |
| RF4-20 | 15 | 12 | 24 | 120 | 91.2 | 91.2 | 89.5 | 5.9 | 16.5 | 13.2 | 59.8 | 85.4 | 0.0/6.0 | <0.01 |
| RF4-30 | 22.5 | 18 | 48 | 246 | 88.6 | 89.7 | 89.4 | 6.4 | 24 | 19.2 | 89.3 | 128.5 | 0.0/6.0 | <0.01 |
| RF4-40 | 30 | 24 | 72 | 373 | 91.0 | 91.8 | 91.0 | 6.6 | 31.5 | 25.2 | 118.7 | 167.9 | 0.0/6.0 | <0.01 |

| CE CERT | FRAME | SAE ENGINE HOUSING | SAE FLYWHEEL | INSULATION CLASS | IP RATING | BEARING KIT |
| --- | --- | --- | --- | --- | --- | --- |
| Yes | 160 | SAE 5* | SAE 7½** | H | IP23 | OPTIONAL |

* Also available in SAE 4 upon request

** Also available in SAE 6½, SAE 8, SAE 10, and SAE 11½ upon request

TYPICAL ELECTRICAL DATA

|  |  | RF4-8 | RF4-16 | RF4-24 | RF4-32 |
| --- | --- | --- | --- | --- | --- |
| Kcc | Short-circuit ratio | 4.57 | 5.25 | 6.47 | 8.08 |
| Xd | Direct-axis synchronous reactance unsaturated | - | - | - | - |
| Xq | Quadrature-axis synchronous reactance unsaturated | - | - | - | - |
| T'd | Short-circuit transient time constant | <0.01 | <0.01 | <0.01 | <0.01 |
| T'do | No-load transient time constant | <0.01 | <0.01 | <0.01 | <0.01 |
| Ω | Stator winding resistance | 0.86 | 0.25 | 0.14 | 0.09 |

DIMENSIONS

Model a b Weight mm mm kg RF4-10 236 189 39 RF4-20 301 223 58 RF4-30 351 273 77 RF4-40 421 343 96

# Text boxes

2/7 PRITCHARD PLACE

PEAKHURST NSW 2210 AUSTRALIA

SALES@RFLATERNATORS.COM

Tel: +61 02 9584 9970   |   WWW.RFLALTERNATORS.COM

RFL ALTERNATORS

RF4 - SERIES

2/7 PRITCHARD PLACE

PEAKHURST NSW 2210 AUSTRALIA

SALES@RFLATERNATORS.COM

Tel: +61 02 9584 9970   |   WWW.RFLALTERNATORS.COM

RF4 - SERIES

PERMANENT MAGNET ALTERNATOR - BRUSHLESS AND AVR-LESS

Tested by STIEE